[image: image3.png]



                                    Category 5e F/UTP 4-pairs PVC 
[image: image1.png]Shturmann




[image: image2.png]



DESIGN
1) Conductor: solid annealed copper
2) Insulation: solid PE
3) Pair: two conductors twisted together

Color identification of pairs: 

· pair 1: white-blue / blue

· pair 2: white-orange / orange

· pair 3: white-green / green

· pair 4: white-brown / brown

4) Core wrapping
5) Copper tinned contact wire Ø 0,4 mm
6) Core shield: aluminum polymer foil (metal outside)
7) Jacket: PVC, color RAL 7035

СOMPLIANCE WITH THE REQUIREMENTS

	Cable: IEC 61156-5 (cat.5e)

Cabling: ISO/IEC 11801-1 & EN 50173-1 (class D), ANSI/TIA 568-С.2 (cat.5e)

Fire safety: IEC 60332-1, CPR class Eca 
	


MECHANICAL CHARACTERISTICS 
	Тemperature range:

· During installation -10 °C ... +60 °C

· After installation -20 °C ... +60 °C
	Bending radius:

· During installation ≥ 8 cable diameters

· After installation ≥ 4 cable diameters 
	Tensile stress ≤ 85 N 




ELECTRICAL CHARACTERISTICS AT 20 °C
	Parameter

	Unit

	Value


	Capacitance

	pF/m

	≤ 56


	Direct current resistance for 

conductors with Ø:

0,51 mm

0,48 mm

0,46 mm

0,44 mm

	Оhm/km

	≤ 92
≤ 103
≤ 112
≤ 123

	Insulation resistance

	GOhm*km

	≥ 5


	Resistance unbalance

	%

	2


	Signal propagation velocity

	s

	0,69


	Characteristic impedance in the 
frequency range of: 1-100 MHz

	Ohm

	100±15

	Test voltage between cores, (DC, 2 s)

	kV

	2,5




	
	Frequency, MHz

1

4

10

16

20

31,25

62,5

100

Attenuation, dB, max; for max. cable lengths with conductor Ø:

0,51 mm = 104 m 
0,48 mm = 92 m
0,46 mm = 84 m
0,44 mm = 77 m
2,1

4,1

6,5
8,3
9,3
11,7
17,0

22,0

NEXT, dB, min
65,3

56,3
50,3
47,2

45,8
42,9
38,4
35,3
PS NEXT, dB, min
62,3

53,3
47,3
44,2

42,8
39,9
35,4
32,3
ELFEXT, dB, min
64
52

44
40

38

34
28
24
PS ELFEXT, dB, min
61

49

41

37

35
31

25
21

RL, dB, min
20,0

23,0

25,0

25,0

25,0

23,3

20,7

19,0

IEC 61156-5, values lower than 4 MHz are given for information only



ORDER INFORMATION

	P/N
	Cable name
	Conductor

Ø, mm
	Insulated conductor Ø, mm
	Outer cable Ø, mm
	Packing
	Weight,

kg/km

	49352-15
	KPVE-VP (200) 4x2x0,51 (F/UTP-cat.5E)
	0,51
	1,03
	5,780
	box, 305 m
	37,135

	49577-11
	KPVE-VP (100) 4x2x0,48 (U/UTP-cat.5E-SL)
	0,48
	0,97
	5,513
	box, 305 m
	34,074

	49559-9
	KPVE-VP (100) 4х2х0,46 (U/UTP-cat.5E-SL)
	0,46
	0,93
	5,357
	box, 305 m
	32,186

	49641-3
	KPVE-VP (100) 4х2х0,44 (U/UTP-cat.5E-SL)
	0,44
	0,89
	5,179
	box, 305 m
	30,316


